## _cm drainback pg1
Pump Float Setting Worksheet - Drainback Metric Version page 1 of 2 |  |  |  |  | All INPUTS are entered into the white boxes
All calculated values are displayed in the blue boxes
INPUTS |  |  |  |  | Changes can only be made to values in white INPUT boxes
Design flow |  | 1360 | L/day
Doses |  | 6 | doses/day
Manufacturer:________________ |  |  |  |  | wall thickness
Nominal tank size |  | 1500 | L
External tank dimensions |  |  |  |  | width
External Length length |  | 150 | cm
External Width width |  | 120 | cm
External Height height |  | 150 | cm
Wall thickness |  | 7.5 | cm
Floor thickness |  | 10 | cm |  | length
External Bottom to Invert of Inlet |  | 150 | cm |  | Plan of Pump Chamber
Weight |  | 1700 | kg
Pump manufacturer, model : _______________________________ |  |  |  |  | Voltage: _________ Amps: ___________
Pump height |  | 50 | cm
Calculated (from above INPUTS)
Internal length |  | 135 | cm |  | = ext length - 2 x wall thickness
Internal width |  | 105 | cm |  | = ext width - 2 x wall thickness
Internal height to the invert |  | 140 | cm |  | = ext bottom to invert of inlet - floor thickness
of the inlet pipe
Internal floor area |  | 14175 | square cm |  | = internal length x internal width
or |  | 1.4175 | square m |  | = internal floor area cm /10000
Volume in 1 cm of depth |  | 14.175 | L |  | = internal floor area in square cm x 1
1 L height = V |  | 0.070547 | cm |  | = 1 / (Volume in 1cm of depth)
or |  | 7.0547e-05 | m |  | = 1 / (Volume in 1cm of depth* 1000)
Alarm reserve volume |  | 680 | L | 50 | % of Daily Design Flow
Reserve volume |  | 204 | L | 15 | % of Daily Design Flow
Dose volume |  | 226.6667 | L |  | = Daily design flow / doses per day
Drainback (DB) | no | 0 | L | 0 | If YES, enter length in metres of 50 mm dia.pipe to calc drainback volume
Pump cooling height |  | 50 | cm |  | = 50% - 100% of pump height, recommend try 100% first
Pump spacer height (input) |  | 4 | cm |  | = selected by designer; recommend 4 - 10 cm

## cm drainback pg2
| Pump Float Setting Worksheet - Drainback Metric Version page 2 of 2 | [8 empty] | Metric Units
[10 empty] | Height above pump | Height above pump
[10 empty] | chamber floor | chamber floor
|  |  |  | V = |  | 0.070547 |  | cm |  | centimetres
Inlet = | 140 | cm
above pump floor | [9 empty] | 132.3539
|  |  |  | Alarm reserve volume (ARV) = |  |  |  | 680
Alarm reserve height = ARV x V
|  |  |  | 680 | X | 0.070547 | = | 47.9718 | + | 47.9718
Alarm float
84.3821
|  |  |  | Reserve volume (RV ) = |  |  |  | 204
Reserve height = RV x V
|  |  |  | 204 | X | 0.070547 | = | 14.3915 | + | 14.3915
| Pump on | [8 empty] | 69.9906
|  |  |  | Dose volume (DV ) = |  |  |  | 226.6667
| Pump range |  |  | Pump range = DV x V
|  |  |  | 226.6667 | X | 0.070547 | = | 15.9906 | + | 15.9906
| 15.9906 | cm
Float tether length
|  | cm |  | Drainback (DB), If NO; DB = 0, |  |  | no | 0 | + | 0
| 8 cm min. |  |  | If YES, Drainback = DB x V
|  |  |  | 0 | X | 0.070547 | = | 0
| Pump off | [8 empty] | 54
|  |  |  | Pump cooling height |  |  | = | 50 | + | 50
4
Pump
|  |  |  | Pump spacer height |  |  | = | 4 | + | 4
[10 empty] | 0 | 0

## _input inches drainbk pg1
Pump Float Setting Worksheet - Drainback Inches Version page 1 of 2 |  |  |  |  | All INPUTS are entered into the white boxes
All calculated values are displayed in the blue boxes
INPUTS |  |  |  |  | Changes can only be made to values in white INPUT boxes
Design flow |  | 300 | Igal/day
Doses |  | 5 | doses/day
Manufacturer :___________________ |  |  |  |  | wall thickness
Nominal tank size |  | 600 | Igal
External tank dimensions |  |  |  |  | width
External Length length |  | 96 | inches
External Width width |  | 50 | inches
External Height height |  | 52 | inches
Wall thickness |  | 3 | inches
Floor thickness |  | 4 | inches |  | length
External Bottom to Invert of Inlet |  | 44 | inches |  | Plan of Pump Chamber
Weight |  |  | pounds
Pump manufacturer, model : _______________________________ |  |  |  |  | Voltage: _________ Amps: ___________
Pump height |  |  | inches
Calculated (from above INPUTS)
Internal length |  | 50 | inches |  | = ext length - 2 x wall thickness
Internal width |  | 44 | inches |  | = ext width - 2 x wall thickness
Internal height to the invert |  | 40 | inches |  | = ext bottom to invert of inlet - floor thickness
of the inlet pipe
Internal floor area |  | 2200 | square inches |  | = internal length x internal width
or |  | 15.2778 | square feet |  | = internal floor area /144
Volume in 1' of depth |  | 95.1806 | Igal |  | = internal floor area in square feet x 6.23
1 Igal height = V |  | 0.12608 | inches |  | = 1 / (12* Volume in 1' of depth)
or |  | 0.010506 | feet |  | = 1 / (Volume in 1' of depth)
Alarm reserve volume |  | 150 | Igal | 50 | % of Daily Design Flow
Reserve volume |  | 45 | Igal | 15 | % of Daily Design Flow
Dose volume |  | 60 | Igal |  | = Daily design flow / doses per day
Drainback (DB) | yes | 35.208 | Igal | 240 | If YES, enter length of 2" pipe to calc drainback volume
Pump cooling height |  | 0 | inches |  | = 50% - 100% of pump height, recommend try 100% first
Pump spacer height (input) |  |  | inches |  | = selected by designer; recommend 1.5 - 4 inches

## pump range vs tether inches
Pump range | Tether length
inches | inches
7 | 3.5
10 | 6
16 | 10
22 | 14
28 | 18
33 | 22
36 | 24

## graph pump vs tether cm
Pump range | Tether length
cm | cm
17.78 | 8.89
25.4 | 15.24
40.64 | 25.4
55.88 | 35.56
71.12 | 45.72
83.82 | 55.88
91.44 | 60.96

## input inches drainback pg2
Pump Float Setting Worksheet - Drainback Inches Version page 2 of 2 | [8 empty] | Imperial Units
[9 empty] | Height above pump | Height above pump
|  |  | V = |  | 0.12608 |  | Inches |  | chamber floor | chamber floor
Inches
Inlet | [8 empty] | 36.5883
|  |  | Alarm reserve volume (ARV) = |  |  |  | 150
Alarm reserve height = ARV x V
|  |  | 150 | X | 0.12608 | = | 18.9114 | + | 18.9114
Alarm float | [8 empty] | 17.6769
|  |  | Reserve volume (RV ) = |  |  |  | 45
Reserve height = RV x V
|  |  | 45 | X | 0.12608 | = | 5.6734 | + | 5.6734
Pump on | [8 empty] | 12.0035
|  |  | Dose volume (DV ) = |  |  |  | 60
Pump range |  |  | Pump range = DV x V
|  |  | 60 | X | 0.12608 | = | 7.5646 | + | 7.5646
12.0035 | inches
Float tether length |  |  | Drainback, If NO; DB = 0, If YES |  |  |  | 35.208 | + | 4.4389
| inches |  | Drainback = DB x V
(3.5 in min) |  |  | 35.208 | X | 0.12608 | = | 4.4389
Pump off | [8 empty] | 0
|  |  | Pump cooling height |  |  | = | 0 | + | 0
0
Pump
|  |  | Pump spacer height |  |  | = | 0 | + | 0
[9 empty] | 0 | 0